12V 24AH

Specification:

LEV24-12

LEV series VRLA battery

LIVEN LEV Series

Cells Per Unit                                             6

Voltage Per Unit                                        12

Nominal Capacity                                      24Ah@20hr-rate to 1.75V per cell @25°C

Weight                                                        Approx. 7.00 Kg ±2% Internal Resistance                                   Approx. 10.0 mΩ Terminal                                                     R5.1

Max. Discharge Current                            288 A (5 sec)

Cold Cranking Ampere (CCA)                  205A

Recommended Maximum Charging

Current                                                       7.2A

AGM   (Absorbent   Glass   Material)   technology   with   gas

recombination. VRLA (Valve Regulated Lead Acid Battery). LEV (Liven Electric Vehicle) series is specially designed for frequent discharge deep cycle application. Maintenance- Free Sealed Lead Acid Battery.

Cycle use 1: Up to 260 cycles at 100% DOD.

Standby Use Voltage                                13.7 V~13.9 V @ 25°C

Temperature Compensation: -3mV/°C/Cell

Cycle Use Voltage                                     14.6 V~14.8 V @ 25°C

Temperature Compensation: -4mV/°C/Cell

Discharge:   -20°C~60°C

Cycle use 2: Up to 500 cycles at 50% DOD.

Application:

Operating Temperature Range

Charge:          0°C~50°C Storage:      -20°C~60°C

•  Electric Vehicle

•  Golf cart

•  Industrial equipment

•  Floor machines

•  Marine

•  RV

•  No-idle solutions

•  Mobility

Normal Operating Temperature Range   25°C±5°C

LIVEN  Valve  Regulated  Lead  Acid  (VRLA)

batteries can be stored for up to 6 months at

•  Forklifts

•  Aerial lifts and Robotics

Dimensions:

•  Medical equipment

•  Outdoor application

Self Discharge

25°C and then recharging is recommended.

Monthly Self-discharge ratio is less than 3%

at 25°C.Please charge batteries before using.

Length                                           181±2mm (7.13 inches) Width                                              77±2mm (3.03 inches) Height                                            170±2mm (6.69 inches) Total Height                                   170±2mm (6.69 inches)

Drawing:

Container Material                                     A.B.S. UL94-HB, UL94-V0 Optional.

| Constant Current Discharge (CC, Unit: A) at 25ºC (77ºF) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F.V/Time | 5MIN | 10MIN | 15MIN | 30MIN | 1HR | 2HR | 3HR | 4HR | 5HR | 8HR | 10HR | 20HR |
| 1.60V | 100.3 | 65.79 | 49.00 | 28.17 | 16.53 | 9.433 | 6.662 | 5.209 | 4.348 | 2.938 | 2.430 | 1.248 |
| 1.65V | 96.63 | 63.59 | 47.53 | 27.58 | 16.22 | 9.273 | 6.561 | 5.138 | 4.294 | 2.905 | 2.406 | 1.237 |
| 1.70V | 91.80 | 60.73 | 45.61 | 26.79 | 15.81 | 9.060 | 6.425 | 5.042 | 4.222 | 2.861 | 2.373 | 1.222 |
| 1.75V | 85.37 | 56.91 | 43.02 | 25.73 | 15.24 | 8.768 | 6.239 | 4.911 | 4.123 | 2.801 | 2.328 | 1.200 |
| 1.80V | 76.83 | 51.79 | 39.54 | 24.27 | 14.47 | 8.366 | 5.981 | 4.728 | 3.985 | 2.717 | 2.265 | 1.171 |
| 1.85V | 65.31 | 44.79 | 34.73 | 22.21 | 13.36 | 7.789 | 5.610 | 4.464 | 3.785 | 2.594 | 2.173 | 1.129 |

| Constant Power Discharge (CP, Unit: W/Battery) at 25ºC (77ºF) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F.V/Time | 5MIN | 10MIN | 15MIN | 30MIN | 1HR | 2HR | 3HR | 4HR | 5HR | 8HR | 10HR | 20HR |
| 1.60V | 1021.2 | 670.8 | 514.0 | 307.0 | 185.5 | 107.3 | 76.4 | 60.0 | 50.3 | 34.4 | 28.7 | 14.8 |
| 1.65V | 1009.2 | 666.0 | 509.0 | 305.0 | 183.9 | 106.2 | 75.7 | 59.5 | 49.9 | 34.1 | 28.4 | 14.6 |
| 1.70V | 969.6 | 643.2 | 492.7 | 298.0 | 179.8 | 104.1 | 74.3 | 58.5 | 49.2 | 33.7 | 28.1 | 14.5 |
| 1.75V | 918.0 | 613.2 | 471.5 | 289.1 | 174.3 | 101.2 | 72.4 | 57.2 | 48.2 | 33.0 | 27.5 | 14.2 |
| 1.80V | 840.6 | 567.8 | 439.4 | 275.5 | 166.2 | 97.1 | 69.7 | 55.3 | 46.7 | 32.1 | 26.9 | 13.9 |
| 1.85V | 727.2 | 499.9 | 391.6 | 254.6 | 154.6 | 90.8 | 65.7 | 52.4 | 44.5 | 30.7 | 25.8 | 13.4 |

12V 24AH                            LEV series VRLA                                    LEV24-12

(Note) All above information shall be changed without prior notice, LIVEN Battery reserves the right to explain and update the latest information.

Charge Characteristic Curve For Cycle Use (IIUU)                              Charge Characteristic Curve For Cycle Use (IUI)

Cycle Life In Relation To Depth Of Discharge                                      Storage Characteristics

Discharge Characteristics Curve                                                          Relationship Between Charging Voltage And Temperature

Relationship of OCV And State of Charge (20ºC)                                Temperature Effects On Capacity

V00 19/02